[image: image32.jpg]FIMDO



 WuhanGoldhomeHipotElectricalCo.,ltd                                www.hvcablehipot.com
 [image: image31.jpg]FIMDO



 WuhanGoldhomeHipotElectricalCo.,ltd                                            www.hvcablehipot.com

OPERATION MANUAL 

 HM801 Transformer Oil BDV Tester

                        [image: image1.jpg]



WUHAN GOLDHOME HIPOT ELECTRICAL CO.,TLD

Tel.：+86-13720265142                              Fax：+86-27-84625205

Email：goldhome03@cablehipot.com                 Web.: www.hvcablehipot.com 

Add.: No.A25-1, Huading Mould Industrial Park, Hannan, Wuhan, Hubei, China

Dear Customers,

Thank you for choosing HM801 Transformer Oil BDV Tester.

We hope that this tester will make your work more easy and pleasant, letting you enjoy office automation during test analysis. 
Please read this User Manual before using the tester, and follow the instructions to operate and maintain it for prolonging its service life. 

The instrument is characterized by “Performing the test automatically by a slight click only”.
I. OVERVIEW
Many power systems, railway systems, large-scale petrochemical plants and enterprises have a lot of electrical equipment whose internal insulation are mostly oil-filled insulation type, and therefore, test on insulating oil dielectric strength is common and necessary. To meet the needs of the market, we have developed and produced a series of insulating oil dielectric strength testers according to national standard GB/T507-2002, industry standard DL429.9-91 and the latest Electric Power Industry Standard DL/T846.7-2004 by ourselves. This instrument, by using a single-chip microcomputer as the core, can operate in full automation with high accuracy, greatly improving work efficiency and reducing the labor intensity of workers. Moreover, it is small in size and convenient to carry.
II. KEY FUNCTION AND FEATURE
1. With a microprocessor, automatically fulfill the withstand voltage test for oil circulation with a range of 0～80KV (including boosting, maintaining, mixing, standing, calculation, printing and other operations) 
2. Display by large-screen LCD and prompt by Chinese menu 

3. Simple operation. The machine will automatically complete the withstand voltage test on one cup of sample oil after simple setting by the operator. Breakdown voltage value of 1 to 9 times and recurrent times will be automatically saved. After the test, the thermal printer will print each breakdown voltage value and average value. 
4. Power-down preservation. It can save 100 tested results. 

5. Adopt a single-chip microcomputer to boost the voltage at an even speed. The voltage is accurate at 50HZ, ensuring the whole process easy for control. 
6. Equipped with over-voltage, over-current and limit protections to ensure the safety of operators.
7. With the function of displaying the measured temperature and system clock.
8. Communicate with computer with a standard RS232 interface.

9、USB， can export the test data.

III. MAJOR TECHNICAL INDICATORS 
1、Output voltage: 0～80KV (optional)        
2、Voltage distortion rate: ＜3%
3、Booster capacity: 1.5KVA
4、Measuring accuracy: ±3％

5、Supply voltage: AC220V±10%   50Hz±1 Hz
6、Power: 200W
7、Applicable temperature: 0℃～45℃
8、Applicable humidity: ＜75%RH
9、Overall dimension: 460×280×320
IV. Operational Approach
1. Preparation before Test
① Connect the earth terminal (on the right side of the equipment) to the earth wire firmly before start the equipment.
② Sample the oil according to relevant standard. Adjust the electrode distance inside the oil cup with standard gauge. Clean the cup according to relevant requirements. Pour the sample into the cup and close the cap.
③ Switch on AC220V power supply after the above items are confirmed, ready for the test.
2. Testing
①  Press the power switch and then enter the following interface:
   [image: image2.png]13:07:45
2018-01-02 TUE

Q@ Em

Set Test Query China




 
②  Set of system parameters:

Press <Set> key and enter the following interface:
  [image: image3.png]@ Settings

Standard Select

@® Custom

O DL/T 846.7-2016
O DL/T 429.9-1991
O GBIT 507-2002
O IEC 60156:1995

System Set

@ Auto-printing
. Device Calibrate
@ Time Setting

. Device Information





1) Standard select
The user can choose the standard of test execution according to the need. 

“[image: image4.png]


” means not to choose，“[image: image5.png]


”means to choose.
The user can go up and down to select other standard.
The user may select based on actual demand and enter the following interface: 
  [image: image6.png]MaxVolt

80kV

UP [DowN

Stand Time | Rest Time
15min 5min

up [pown | P [pown

Test Count [ Volt.rate

6times | 3.0kV/s
up [powN | Up [powN





[image: image31.jpg]Max.Volt: 10～80KV   
Stand Time: 0～15min          
Rest Time: 0～5min       
Stir Time: 0～120sec. Always          

Test Count: 1～10 
Volt.rate: 0.5 KV/S～5.0 KV/S
If you choose another standard, for example: 

  [image: image7.png]@ Settings

Standard Select

© |pL/T 84672016
Max.Volt: 0KV

Stand Time: Smin
O | Rest time: 2min
O | Test Count: 6 Gap: 2.5mm|
Sy Electrodes: Sph/Mn:

@ | st Time: 1 min +

@ | Voltrate: 2.0kVis 3.0kVs |

@ Time Setting >
@

nformation





Stir time and Volt.rate are optional. After selecting, click “[image: image8.png]


” to return.
2) System set 

(1)Autotype: ON/OFF，select by button
“[image: image9.png]


” means not to choose，“[image: image10.png]


”means to choose
(2)Time setting：When the instrument time is not accurate, can be adjusted
(3) Device Calibrate：Generally, users do not need to calibrate the instrument
(4)Device Information You can view the device version, factory and other information
When setting is complete, click “[image: image11.png]


” to save the settings and return to the main interface.
③  Test
 Press the <Test> key to enter the following interface:
  [image: image12.png]52 Standing

Standard: Custom

Countdown(s): A

o8

Max.Volt: 80KV Test Count: 6
Stir Time: 105 [Auto Print: ON

Volt.rate:2.0 kV/s
Rest time: 3005





After the static time is over, enter the boost interface automatically. Click "start" button to skip the static entry and enter the boost interface. Click “[image: image13.png]


” to exit the test interface and return to the main interface.
  [image: image14.png]Mean: 45.63kV A

36. 85kv

OODD

Max.Volt: 80KV Test Count: 6
Stir Time: 105 [Auto Print: ON
Volt.rate:2.0 kV/s

Rest time: 3005





If you click the <Stop> button, then stop the rise voltage

If you click the <Rise> button, then the voltage rises
If you click the <fall> button, then voltage drop
The first test ended, enter the delay interface
  [image: image15.png]() Stirring & Delaying
Standard: Custom

Countdown(s): A

300

Max.Volt: 80KV [Test Count: 6
Stir Time: 105 |Auto Print: ON

Voltrate:2.0kV/s
Rest Time: 300 s
Stand Time: 15 min





After the delay, the next test starts until the boosting frequency is reached. Finally, the result is showed as follows:
Click[image: image16.png]


 to enter the sample number，and  click “OK”to store the data.
  [image: image17.png]45.63kV
14489V 2] 42,09V
3]4135KV 414177k

S5]41.03KV 6] 42.79kV

1 2 3

4 5 6

7 8 9
OK 0 ESC




  [image: image18.png]e Test Result

Sample No: 123456
Mean: 4178KV.

1J4489KV 2] 42.09KV
413KV 441K

SILOBKY 6] 4279KV

Std.Dev.: 075KV
cv.: 0004
Standard:  Custom





④ Data Query:

   Press the <Query> key to enter the following interface:
  [image: image19.png]e Data Query @

SumpleNos [ 3650
Mean: [y 24/

14489KY 2] 42.09KV.

413K 441KV
SJLOIKY 6] 4279KV

M) 2 R g

PgUp PgDn Print Del USB





Select “[image: image20.png]


” Page Up，Select “[image: image21.png]


”Page Down，

Select the records to be printed and select “[image: image22.png]


”, 

Select “[image: image23.png]


”to delete data from the current page. 
Select "[image: image24.png]


" insert U disk, USB export data. 

Select” [image: image25.png]


”to empty the data.
V. Precautions
1. The selection, placing and electrode distance of the oil sample before testing shall meet relevant national and industrial standards.
2. The operators or other personnel are strictly forbidden to touch the casing after the power is switched on to avoid accidents.
3. The power shall be cut off immediately if any abnormal event is found during the operation.
4. New oil cup or cleaning the oil cup should be 24 times breakdown after test execution. When oil cup don't do experiments should use clean oil immersion
VI. Maintenance
1. This equipment shall not be exposed in moist environment.
2. Keep the oil cup and the electrodes clean. Fill the cup with fresh transformer oil for protection during its idle. Check the electrode distance and check the tightness between the electrode tip and electrode bar screw thread before the cup is used again.
VII. Oil Cup Cleaning Method and Common Fault Clearances
1. Oil Cup Cleaning Method
⑴ Wipe the electrode surfaces and bars again and again with clean silk cloth.
⑵ Adjust the electrode distance with standard gauge.

⑶ Use petroleum ether (other organic solvents are forbidden) to clean thrice. Each time shall follow the bellow procedures:
Pour the petroleum ether into the oil cup till the cup is 1/4～1/3 full.
② Cover the cup mouth with a piece of glass cleaned by petroleum ether. Shake the cup evenly for one minute with certain force.
③ Pour away the petroleum ether and dry the cup with a blower for 2~3 minutes.
⑷ Use the oil sample to be tested to clean the cup for 1~3 times.
① Pour the petroleum ether into the oil cup till the cup is 1/4～1/3 full. 

② Cover the cup mouth with a piece of glass cleaned by petroleum ether. Shake the cup evenly for one minute with certain force.
③ Pour away the left oil sample and then the test starts.
2. Agitating Blade Cleaning Method
⑴ Wipe the agitating blade again and again with clean silk cloth until fine particles are not found on their surfaces. It is forbidden to touch the surfaces with hands.
⑵ Use forceps to clamp the blade; put them into petroleum ether and wash.
⑶ Use forceps to clamp the blade and dry them with a blower.
⑷ Use forceps to clamp the blade; put them into the oil sample to be tested and wash.
3. Oil Cup Storage
Method 1 Fill the cup with good insulating oil after the test is finished and place it stable.
Method 2 Clean and dry the cup under the above procedures and then put it into a vacuum dryer.
Note: The oil cup and agitating blade shall be cleaned under the above procedures after the first test and tests with poor oil.
4. Common Fault Clearances
⑴ Power light off, screen display off
① Check the plugging of power plug.
② Check the condition of the protector tube inside the power plug.
③ Check the socket electricity.
⑵ No punch through oil cup
① Check inserting of connectors on circuit board.
② Check contacting of cap high-voltage switch.
③ Check attracting of high-voltage contacts.
④ Check break of high-voltage line.
⑶ Printer failure
① Check plugging of printer power line.
② Check plugging of printer data line.

Ⅷ、Appendix: Instrument calibration

1. Click on the “Instrument Calibration” enter the password input interface, as shown below:

  [image: image26.png]() Screen Lock

Please enter the unlock code

1

IS
o | w|
N

oK ESC




Enter the password: 1397

2. Enter the password to enter the following interface
  [image: image27.png]. Device Calibration





1)． Click <Calibration Data>, enter the historical calibration data storage interface.

  [image: image28.png]e Calibration Data

No.| Grade|  Actual | Measured

10 99 98

20 | 196 | 193

30 | 301 [ 298

40 | 405 | 402

50 | 503 | s0s

60 | 504 | so8

70 | 700 | 704

80 | 807 | 804

Tint k.




"Actual" is the measured value of the instrument. "Measured" is the value of the multimeter display, and the data can be modified by clicking on any value.
If the user needs to recalibrate the data, the calibrated data needs to be initialized first and then click <Initialization>. 

If the user needs to restore the factory data, click <Factory>.
2). Click <Start Calibration> enter the instrument calibration interface
  [image: image29.png]@ Device Calibration
Picaseconnectthe valage divider

Voltage rise to: (B0 kv ‘

a8. a8
kv





Connect the voltage divider, multimeter, click <Start> button to boost, the interface is as follows:
  [image: image30.png]@ Device Calibration
Please connect the voltage dvider T

Voltage s 0§DV ‘

35.47
kv





When the instrument voltage rises to the data to be tested, click the <Stop> key to record the instrument display value and multimeter display value, and then click the <Start> key instrument will continue to boost until the test is completed click the Back button, the test Data is entered in "Data Calibration" for storage.

7

[image: image32.jpg]